## Constants
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
20000 | shelf_no | 1 | WORD | 10 | x
| shelf_reg_size | 1 | WORD | 50 | x
| snsr_no | 1 | WORD | 152
| snsr_data_reg_size | 1 | WORD | 6

## Shelf
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
10000 | Addr | 1 | WORD | 0
| lightIntensOut | 1 | WORD | 0
| lightOnOut | 1 | BOOL | FALSE
| PV_PosArr | 3 | ARRAY [3] OF WORD | [3(0)]
| e_PV_OnArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)]
| e_PV_PresArr | 3 | ARRAY [3] OF WORD | [3(0)]
| e_lightIntensity | 1 | WORD | 0
| e_lightOn | 1 | BOOL | FALSE
| mode | 1 | WORD | 2 | x
| a_waterOn | 1 | BOOL | FALSE | x
| a_lightOn | 1 | BOOL | FALSE | x
| a_PV_EnableArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| a_PV_PresArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| a_lightIntensity | 1 | WORD | 0 | x
| m_PV_OnArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| m_PV_PresArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| m_lightIntensity | 1 | WORD | 0 | x
| m_lightOn | 1 | BOOL | FALSE | x
| m_PV_PosArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| o_lightIntensity | 1 | WORD | 0 | x
| o_lightOn | 1 | BOOL | FALSE | x
| o_PV_PosArr | 3 | ARRAY [3] OF WORD | [3(0)] | x

## Sensor List
base_addr | shelf_sensor | general_sensor
12000 | wPres0 | wFlow0
| wPres1 | wFlow1
| wPres2 | aFlow0
| wTemp0 | aFlow1
| wTemp1 | aFlow2
aFlow3
aFlow4
aFlow5
aFlow6
aFlow7
aFlow8
aFlow9
aFlow10
aFlow11
aFlow12
aFlow13
aFlow14
aFlow15
aFlow16
aFlow17
aFlow18
aFlow19
aFlow20
aFlow21
aFlow22
aFlow23
aFlow24
aTemp0
aTemp1
aTemp2
aTemp3
aTemp4
aTemp5
aTemp6
aTemp7
aTemp8
aTemp9
aTemp10
aTemp11
aTemp12
aTemp13
aTemp14
aTemp15
aTemp16
aTemp17
aTemp18
aTemp19
aTemp20
aTemp21
aTemp22
aTemp23
aTemp24
aCO2_0
aCO2_1
aCO2_2
aCO2_3
aCO2_4
aCO2_5
aCO2_6
aCO2_7
aCO2_8
aCO2_9
aCO2_10
aCO2_11
aCO2_12
aCO2_13
aCO2_14
aCO2_15
aCO2_16
aCO2_17
aCO2_18
aCO2_19
aCO2_20
aCO2_21
aCO2_22
aCO2_23
aCO2_24
aRH_0
aRH_1
aRH_2
aRH_3
aRH_4
aRH_5
aRH_6
aRH_7
aRH_8
aRH_9
aRH_10
aRH_11
aRH_12
aRH_13
aRH_14
aRH_15
aRH_16
aRH_17
aRH_18
aRH_19
aRH_20
aRH_21
aRH_22
aRH_23
aRH_24

## Sensor Data
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
- | value | 1 | WORD | 0
| state | 1 | WORD | 0
| err_u | 1 | WORD | 0
| warn_u | 1 | WORD | 0
| warn_l | 1 | WORD | 0
| err_l | 1 | WORD | 0

## Pump
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
11000 | pump_e_OnArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_e_RpmValArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_e_ValveOnArr | 1 | ARRAY [4] OF BOOL | [4(FALSE)] | x
| pump_e_FlowOrRpm | 1 | WORD | 0 | x
| pump_h_Mode | 1 | WORD | 0 | x
| pump_h_PumpSelect | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_h_FlowSetArr | 2 | ARRAY [2] OF WORD | [2(0)] | x
| pump_h_RpmSetArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_h_ValveOnArr | 1 | ARRAY [4] OF BOOL | [4(FALSE)] | x
| pump_h_RedundantPumpSelect | 1 | WORD | 0 | x
| pump_isRunningArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_modeArr | 3 | ARRAY [3] OF WORD | [3(0)] | x

## IO Mapping
variable_name | addr | type | init_value | hmi_tag | comment
IO_waterPres_s0_0 | D28002 | WORD | -1
IO_waterPres_s0_1 | D28004 | WORD | -1
IO_waterPres_s0_2 | D28006 | WORD | -1
IO_waterPres_s1_0 | D28008 | WORD | -1
IO_waterPres_s1_1 | D28010 | WORD | -1
IO_waterPres_s1_2 | D28012 | WORD | -1
IO_waterPres_s2_0 | D28014 | WORD | -1
IO_waterPres_s2_1 | D28016 | WORD | -1
IO_waterPres_s2_2 | D28022 | WORD | -1
IO_waterPres_s3_0 | D28024 | WORD | -1
IO_waterPres_s3_1 | D28026 | WORD | -1
IO_waterPres_s3_2 | D28028 | WORD | -1
IO_waterPres_s4_0 | D28030 | WORD | -1
IO_waterPres_s4_1 | D28032 | WORD | -1
IO_waterPres_s4_2 | D28034 | WORD | -1
IO_waterPres_s5_0 | D28036 | WORD | -1
IO_waterPres_s5_1 | D28042 | WORD | -1
IO_waterPres_s5_2 | D28044 | WORD | -1
IO_waterPres_s6_0 | D28046 | WORD | -1
IO_waterPres_s6_1 | D28048 | WORD | -1
IO_waterPres_s6_2 | D28050 | WORD | -1
IO_waterPres_s7_0 | D28052 | WORD | -1
IO_waterPres_s7_1 | D28054 | WORD | -1
IO_waterPres_s7_2 | D28056 | WORD | -1
IO_waterPres_s8_0 | D28062 | WORD | -1
IO_waterPres_s8_1 | D28064 | WORD | -1
IO_waterPres_s8_2 | D28066 | WORD | -1
IO_waterPres_s9_0 | D28068 | WORD | -1
IO_waterPres_s9_1 | D28070 | WORD | -1
IO_waterPres_s9_2 | D28072 | WORD | -1
IO_flowmeter_0 | D28082 | WORD | -1
IO_flowmeter_1 | D28084 | WORD | -1
IO_propValve_s0_0 | D28102 | WORD | -1
IO_propValve_s0_1 | D28104 | WORD | -1
IO_propValve_s0_2 | D28106 | WORD | -1
IO_propValve_s1_0 | D28108 | WORD | -1
IO_propValve_s1_1 | D28122 | WORD | -1
IO_propValve_s1_2 | D28124 | WORD | -1
IO_propValve_s2_0 | D28126 | WORD | -1
IO_propValve_s2_1 | D28128 | WORD | -1
IO_propValve_s2_2 | D28142 | WORD | -1
IO_propValve_s3_0 | D28144 | WORD | -1
IO_propValve_s3_1 | D28146 | WORD | -1
IO_propValve_s3_2 | D28148 | WORD | -1
IO_propValve_s4_0 | D28162 | WORD | -1
IO_propValve_s4_1 | D28164 | WORD | -1
IO_propValve_s4_2 | D28166 | WORD | -1
IO_propValve_s5_0 | D28168 | WORD | -1
IO_propValve_s5_1 | D28182 | WORD | -1
IO_propValve_s5_2 | D28184 | WORD | -1
IO_propValve_s6_0 | D28186 | WORD | -1
IO_propValve_s6_1 | D28188 | WORD | -1
IO_propValve_s6_2 | D28202 | WORD | -1
IO_propValve_s7_0 | D28204 | WORD | -1
IO_propValve_s7_1 | D28206 | WORD | -1
IO_propValve_s7_2 | D28208 | WORD | -1
IO_propValve_s8_0 | D28222 | WORD | -1
IO_propValve_s8_1 | D28224 | WORD | -1
IO_propValve_s8_2 | D28226 | WORD | -1
IO_propValve_s9_0 | D28228 | WORD | -1
IO_propValve_s9_1 | D28242 | WORD | -1
IO_propValve_s9_2 | D28244 | WORD | -1
IO_waterLevel_0 | X1.0 | BOOL | FALSE
IO_waterLevel_1 | X1.1 | BOOL | FALSE
IO_waterLevel_2 | X1.2 | BOOL | FALSE
IO_waterLevel_3 | X1.3 | BOOL | FALSE
IO_waterLevel_4 | X1.4 | BOOL | FALSE
IO_waterLevel_5 | X1.5 | BOOL | FALSE
IO_clogSensor_0 | X1.6 | BOOL | FALSE
IO_clogSensor_1 | X1.7 | BOOL | FALSE
IO_solenoid_0 | Y1.0 | BOOL | FALSE
IO_solenoid_1 | Y1.1 | BOOL | FALSE
IO_solenoid_2 | Y1.2 | BOOL | FALSE
IO_solenoid_3 | Y1.3 | BOOL | FALSE
IO_pumpContact_0 | Y1.4 | BOOL | FALSE
IO_pumpContact_1 | Y1.5 | BOOL | FALSE
IO_pumpContact_2 | Y1.6 | BOOL | FALSE
MB_pump0_wStartStop | D26000 | WORD | -1
MB_pump0_wFreqCmd | D26001 | WORD | -1
MB_pump0_wInputSrc | D26005 | WORD | -1
MB_pump0_wPidFbkTerm | D26002 | WORD | -1
MB_pump0_wPidTrgtSrc | D26003 | WORD | -1
MB_pump0_wPidTrgtVal | D26004 | WORD | -1
MB_pump0_rOutputHz | D25102 | WORD | -1 | x
MB_pump0_rAciVal | D25112 | WORD | -1
MB_pump0_rVfdStatus | D25001 | WORD | -1
MB_pump0_rVfdMode | D25135 | WORD | -1
MB_pump1_wStartStop | D26010 | WORD | -1
MB_pump1_wFreqCmd | D26011 | WORD | -1
MB_pump1_wInputSrc | D26015 | WORD | -1
MB_pump1_wPidFbkTerm | D26012 | WORD | -1
MB_pump1_wPidTrgtSrc | D26013 | WORD | -1
MB_pump1_wPidTrgtVal | D26014 | WORD | -1
MB_pump1_rOutputHz | D25302 | WORD | -1 | x
MB_pump1_rAciVal | D25312 | WORD | -1
MB_pump1_rVfdStatus | D25201 | WORD | -1
MB_pump1_rVfdMode | D25335 | WORD | -1
MB_pump2_wStartStop | D26020 | WORD | -1
MB_pump2_wFreqCmd | D26021 | WORD | -1
MB_pump2_wInputSrc | D26025 | WORD | -1
MB_pump2_wPidFbkTerm | D26022 | WORD | -1
MB_pump2_wPidTrgtSrc | D26023 | WORD | -1
MB_pump2_wPidTrgtVal | D26024 | WORD | -1
MB_pump2_rOutputHz | D25502 | WORD | -1 | x
MB_pump2_rAciVal | D25512 | WORD | -1
MB_pump2_rVfdStatus | D25401 | WORD | -1
MB_pump2_rVfdMode | D25535 | WORD | -1

## HMI Internal
base_addr | var_name | var_type | addr_offset | comment
1000 | PUMP_0_SELECTED | BIT | 1
| PUMP_1_SELECTED | BIT | 1
| PUMP_2_SELECTED | BIT | 1
| PUMP_CHECK | WORD | 1
| PUMP_LOCK_SEMI_PART | BIT | 1
| PUMP_LOCK_MANU_PART | BIT | 1
| DUMMY_BIT | BIT | 1
| STRING | WORD | 20
| DUMMY_BIT_TRUE | BIT | 1
| DUMMY_BIT_FALSE | BIT | 1